# Pipe Flow Simulation Report — Water Distribution System

CASE 1

Name: UGWOKE KENECHUKWU PERFECTUS
Reg. No.: 2022/241806

SUMMARY

A steady-state hydraulic simulation of a simple water distribution network was performed using Pipe Flow Expert. The working fluid is water at 20°C. The model contains eight pipe runs (P1–P8), several fittings (tees, bends, globe valves, pipe entries/exits) and nine nodes (N1–N9). Results include node pressures, per-pipe flow rates and velocities, pressure losses (dP), fitting K-values, and an energy loss breakdown by pipe. Key findings: (1) the network delivers the simulated volumetric flows shown in Table 1 while maintaining positive pressures at most nodes; (2) certain pipes and fittings contribute disproportionately to head/energy losses; and (3) the output contains some unexpected entries (e.g., unusually large “length” values recorded in inches) that should be checked in the model input. All numerical values in this report are taken from the Pipe Flow Expert simulation output.

NAME: UGWOKE, KENECHUKWU PERFECTUS

REG. NUMBER: 2022/241806

Pipe Flow Simulation Report – Project 1

1. Summary

A piping system simulation was conducted using Pipe Flow Expert to analyze fluid flow, pressure distribution, and energy losses. The system consists of 7 pipes with associated fittings and a centrifugal pump. The working fluid is water at 20°C.

This report integrates the design data (planned pipe lengths and fixtures) with the simulated results (pressures, flows, losses). Key findings show the pump operates below its best efficiency point, and several pipes, particularly P7, exhibit high energy losses due to velocity and multiple restrictive fittings.

2. Fluid Properties

| Property | Value |
| --- | --- |
| Fluid | Water (H₂O) |
| Temperature | 20°C |
| Density | 998.000 kg/m³ |
| Viscosity | 1.002 cP |

3. Pump Performance

| Parameter | Value |
| --- | --- |
| Pump Name | Pump (Generic) |
| Speed | 2950 rpm |
| Flow Rate | 0.0226 m³/sec |
| Head | 47.633 m |
| Efficiency | 61.70% |
| Power | 17.05 kW |

The pump operates at 61.70% efficiency, which is below its Best Efficiency Point (BEP) of 64.0%.

4. Pipe Network: Design vs. Simulated Results

The following table contrasts the design input (from the provided image) with the simulated output (from Pipe Flow Expert).

Note on Lengths: There is a significant discrepancy between the design and simulated pipe lengths. The simulated model likely includes equivalent lengths for fittings, elevation changes, and other complexities, resulting in much larger values.

5. Fittings Analysis & Losses

The design data correctly identifies the critical fixtures. The simulation confirms that P7, which includes a Globe Valve (K=2.70), Branch Tee (K=1.08), and a pipe exit (K=1.00), has the highest combined fitting loss (0.975 kW), contributing significantly to its total pressure drop.

6. Node Pressure Summary

| Node ID | Type | Elevation (m) | Pressure (bar.g) |
| --- | --- | --- | --- |
| N1 (Tank) | Inlet | 0.000 | 0.2936 |
| N2 | After Pump | 0.000 | 4.8372 |
| N7 (Tank) | Outlet | 17.000 | 0.0000 |
| System Total Pressure Loss (N1 to N7) |  |  | ~4.837 bar |

7. Energy Loss Breakdown

| Pipe ID | Friction Loss (kW) | Fitting Loss (kW) | Total Loss (kW) | Key Contributing Factor |
| --- | --- | --- | --- | --- |
| P1 | 0.224 | 0.042 | 6.797 | Pump Inefficiency |
| P2 | 0.359 | 0.043 | 2.169 | Friction in long pipe |
| P3 | 0.909 | 0.017 | 0.926 | Friction |
| P4 | 1.014 | 0.010 | 1.122 | Friction |
| P5 | 0.334 | 0.012 | 0.346 | Low |
| P6 | 0.813 | 0.012 | 0.937 | High velocity (2.656 m/s) |
| P7 | 0.879 | 0.975 | 2.906 | Multiple Fittings & High Velocity (4.974 m/s) |

8. Conclusions and Recommendations

- Pump Operation: The pump is operating slightly below its BEP. Consider impeller trimming or speed adjustment to improve efficiency and reduce energy costs.

- Critical Line (P7): This line has the highest velocity and fitting-related energy losses.

  - Recommendation: Investigate if the pipe diameter can be increased to reduce velocity.

  - Consider replacing the high-loss Globe Valve with a more efficient valve type (e.g., a ball valve) if feasible for the application.

- High Friction Losses: Pipes P3, P4, and P6 show significant friction losses. The simulated lengths are extremely long, suggesting a significant pressure drop due to pipe run and elevation gain. Verify the routing and overall system layout.

- System Balance: The pressure distribution shows the system is hydraulically functional, but energy optimization is possible.

SYSTEM